{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Estimator","Instructions"],"not_rendered":{"charts":0,"images":5,"macros":1,"external_links":0,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Estimator","index":0,"n_rows":101,"n_cols":13,"rows_kept":101,"cut":false,"hidden":false,"merged":[[29,4,29,9],[17,5,17,6],[19,5,19,6],[21,5,21,6],[25,4,25,9],[26,4,26,9],[27,4,27,9],[28,4,28,9],[3,1,3,2],[24,4,24,9],[23,4,23,9],[3,6,3,8],[0,4,1,7]]}
[null,null,null,null," Active Harmonic Filter Sizing "]
[]
[null,null,"CUSTOMER INPUT"]
[null,null,null,null,null,null,"SYSTEM w/HPS TruWave"]
[null,"Non-Linear Loads",null,null,null,null,null,null,"System with"]
[null,"Total Non-Linear Loads HP:",480,null,null,"SYSTEM w/o","System with","System with","0% TDD"]
[null,"% DC Bus Choke Reactance (Z_DC):",4,null,null,"HPS TruWave","acceptable TDD","0% TDD","& acceptable PF"]
[null,"% Input Line Reactance (Z_LINE):",0.5,null,"RMS Current:",506.62560000000002,466.25448649310863,465.67275889728069,465.67275889728069]
[null,"Acceptable TDD:",5,null,"Fundamental Current:",465.67275889728069,465.67275889728103,465.67275889728069,465.67275889728069]
[null,"Acceptable Displacement PF:",0.95,null,"Harmonic Current:",199.54543391507374,23.283637944864036,0,0]
[null,null,null,null,"TDD%:",42.850999999999999,5,0,0]
[null,null,null,null,"Reactive Current:",208.18417256258911,63.752625868761882,59.348711099861426,59.348711099861426]
[null,"Linear Loads",null,null,"AHF Current:",0,176.2617959702097,199.54543391507374,199.54543391507374]
[null,"Total Linear Motor Loads HP:",0,null,"I_r:",461.87536075199995,461.87536075199995,461.87536075199995,461.87536075199995]
[null,"Linear Motor Loads PF:",0,null,"I_d:",59.348711099861426,59.348711099861426,59.348711099861426,59.348711099861426]
[null,"Resistive Loads kW:",0,null,"Power Factor:",0.91166999999999998,0.99060786358530106,0.99184535046827083,0.99184535046827083]
[]
[null,"Total Linear PF:",0,null,null,"Estimated Size of HPS TruWave"]
[null,null,null,null,null,199.54543391507374,"amps"]
[null,null,null,null,null,"Select appropriate HPS TruWave model"]
[]
[null,null,null,null,null,"based on this estimate."]
[]
[null,"I_RMS:",105.547,null,"Information presented here is for estimating purposes only and does not imply any guarantee of performance or results."]
[null,"TDD:",42.850999999999999,null,"The HPS TruWave may not operate properly if any power factor correction capacitors, or line input filters, are installed on the load  "]
[null,"PF:",0.91166999999999998,null,"side of the HPS TruWave current sensors."]
[null,"kW:",79.998999999999995,null,"Consult factory for any questions regarding the presence of power factor correction capacitors, or line input filters, on your system."]
[null,"kVA:",87.751000000000005,null,"All non-linear loads must have an input line reactor (min. 3%) or a DC link choke (min. 4%) to achieve desired system performance."]
[null,null,null,null,"A THD (V) of less than 5% can be achieved if TDD (I) is less than 5%."]
[]
[]
[null,"%ZDC","%LINE","Ih(A)","%THD-F","P.F.","KW","KVA","IRMS","IF","R1","IR","PAGE"]
[null,0,2,55.2,56.241999999999997,0.85540000000000005,79.998999999999995,93.522000000000006,112.49,98.147999999999996,5.1669799999999997,null,"9-H3"]
[null,0,3,43.578499999999998,44.225999999999999,0.89419999999999999,80.007999999999996,89.474000000000004,107.62,98.534999999999997,5.0848599999999999,null,"12-H2"]
[null,0,4,37.847000000000001,38.201000000000001,0.91080000000000005,80.007000000000005,87.843000000000004,105.658,99.072000000000003,5.0141499999999999,null,"10-H1"]
[null,0,5,34.424999999999997,34.594000000000001,0.91669999999999996,79.998999999999995,87.27,104.97,99.510999999999996,4.95,null,"12-H3"]
[null,0,6,31.99,31.991,0.92020999999999997,79.998000000000005,86.935000000000002,104.566,99.998999999999995,4.8879999999999999,null,"10-H3"]
[null,0,7,30.1325,29.963999999999999,0.92079999999999995,80.001999999999995,86.881,104.502,100.56100000000001,4.8278100000000004]
[null,0,8,28.6585,28.367999999999999,0.9204,80.001000000000005,86.917000000000002,104.545,101.024,4.7697000000000003]
[null,0,9,27.453700000000001,27.038,0.9194,80.001000000000005,87.013999999999996,104.66200000000001,101.53700000000001,4.7133700000000003]
[null,0,10,26.326000000000001,25.797999999999998,0.91779999999999995,80.004999999999995,87.167000000000002,104.846,102.04600000000001,4.6574999999999998]
[null,0,11,25.425599999999999,24.792999999999999,0.91590000000000005,80.001999999999995,87.347999999999999,105.06399999999999,102.551,4.6028799999999999]
[null,1,1,64.534000000000006,66.08,0.81769999999999998,79.995999999999995,97.870999999999995,117.72,97.658000000000001,5.2396000000000003,null,"16-H3"]
[null,1,2,46.575000000000003,47.581000000000003,0.8891,79.997,89.977999999999994,108.227,97.885000000000005,5.1717000000000004,null,"15-H1"]
[null,1,3,39.475000000000001,40.128,0.91020000000000001,79.997,87.888000000000005,105.71299999999999,98.373000000000005,5.0797999999999996,null,"15-H2"]
[null,1,4,35.426000000000002,35.801000000000002,0.91886999999999996,80.006,87.07,104.729,98.951999999999998,5.0129999999999999,null,"15-H3"]
[null,1,5,32.808999999999997,32.996000000000002,0.92179999999999995,80.001999999999995,86.787999999999997,104.39,99.433000000000007,4.9507000000000003,null,"16-H1"]
[null,1,6,30.837,30.855,0.92310000000000003,79.998999999999995,86.662999999999997,104.24,99.941999999999993,4.8905000000000003,null,"16-H2"]
[null,1,7,29.315999999999999,29.186,0.92281999999999997,79.998000000000005,86.688000000000002,104.27,100.444,4.8310750000000002,96.222999999999999,"5-H1"]
[null,1,8,28.04,27.774999999999999,0.92190000000000005,80.001000000000005,86.78,104.38,100.95399999999999,4.7732999999999999,96.225999999999999,"5-H2"]
[null,1,9,26.975999999999999,26.585000000000001,0.92076000000000002,80.001000000000005,86.885000000000005,104.50700000000001,101.47,4.7164419999999998,96.225999999999999,"5-H3"]
[null,1,10,25.937000000000001,25.431999999999999,0.91890000000000005,79.998999999999995,87.057000000000002,104.71299999999999,101.986,4.6608599999999996,96.224000000000004,"1-H1"]
[null,1,11,25.122,24.512,0.91679999999999995,80.001999999999995,87.257999999999996,104.955,102.488,4.6062200000000004,96.227000000000004,"1-H2"]
[null,2,0.5,61.149000000000001,62.933,0.83575999999999995,79.998000000000005,95.718999999999994,115.13200000000001,97.164000000000001,5.2591999999999999,null,"8-H2"]
[null,2,1.5,44.718000000000004,45.795000000000002,0.89742,79.998999999999995,89.143000000000001,107.223,97.647999999999996,5.1783999999999999,null,"8-H3"]
[null,2,2,41.037999999999997,41.945999999999998,0.90720000000000001,80.001999999999995,88.185000000000002,106.07,97.834999999999994,5.14323,null,"11-H3"]
[null,2,3,36.5,37.137999999999998,0.92010000000000003,79.998000000000005,86.944999999999993,104.57899999999999,98.283000000000001,5.0767300000000004,null,"9-H1"]
[null,2,4,32.932000000000002,33.322000000000003,0.92400000000000004,79.998000000000005,86.58,104.14,98.831999999999994,5.0135199999999998,null,"12-H2"]
[null,2,5,31.491,31.681999999999999,0.92620000000000002,80,86.373999999999995,103.892,99.397000000000006,4.9518000000000004,null,"11-H2"]
[null,2,6,29.936,29.978000000000002,0.92610000000000003,80.003,86.388999999999996,103.91,99.858000000000004,4.8915660000000001,96.228999999999999,"3-H1"]
[null,2,7,28.632000000000001,28.515000000000001,0.92520000000000002,80.003,86.471000000000004,104.009,100.40900000000001,4.8332499999999996,96.228999999999999,"3-H2"]
[null,2,8,27.48,27.235700000000001,0.92379999999999995,80.001999999999995,86.602000000000004,104.166,100.89700000000001,4.7757500000000004,96.227000000000004,"3-H3"]
[null,2,9,26.521999999999998,26.155000000000001,0.92164999999999997,80.004000000000005,86.805000000000007,104.41,101.40600000000001,4.7196699999999998,96.23,"4-H1"]
[null,2,10,25.632999999999999,25.15,0.91959999999999997,80.001999999999995,86.995999999999995,104.64,101.922,4.6640699999999997,96.227000000000004,"4-H2"]
[null,2,11,24.818000000000001,24.227,0.91725999999999996,80.004000000000005,87.22,104.91,102.43899999999999,4.6092550000000001,96.23,"4-H3"]
[null,3,0.5,48.302,49.813000000000002,0.88793999999999995,80.001000000000005,90.096999999999994,108.37,96.965999999999994,5.2381000000000002,null,"2-H2"]
[null,3,1.5,39.79,40.795999999999999,0.91478000000000004,80,87.451999999999998,105.18899999999999,97.533000000000001,5.1699000000000002,null,"2-H1"]
[null,3,2,39.893000000000001,40.814,0.91935,80.003,87.021000000000001,104.67,97.742999999999995,5.1375999999999999,null,"11-H1"]
[null,3,3,34.363,34.985999999999997,0.92678000000000005,79.998000000000005,86.319000000000003,103.825,98.218999999999994,5.0744999999999996,null,"1-H2"]
[null,3,4,32.177999999999997,32.584000000000003,0.92825000000000002,79.989999999999995,86.173000000000002,103.65,98.754000000000005,5.0130400000000002,null,"11-H2"]
[null,3,5,30.503,30.689,0.92895000000000005,80.040999999999997,86.162999999999997,103.637,99.394000000000005,4.95,null,"3-H1"]
[null,3,6,29.172999999999998,29.228999999999999,0.92769999999999997,79.995999999999995,86.230999999999995,103.72,99.808000000000007,4.8940000000000001,96.22,"1-H1"]
[null,3,7,28.045999999999999,27.957000000000001,0.9264,79.998000000000005,86.355999999999995,103.72,100.32,4.8354999999999997,96.221999999999994,"1-H2"]
[null,3,8,27.038,26.81,0.9264,80,86.522000000000006,104.07,100.84,4.7784000000000004,96.224999999999994,"1-H3"]
[null,3,9,26.158000000000001,25.808,0.92259999999999998,80,86.712999999999994,104.3,101.357,4.7221200000000003,96.224999999999994,"2-H1"]
[null,3,10,25.338000000000001,24.87,0.92035999999999996,79.998999999999995,86.921000000000006,104.55,101.87,4.6666699999999999,96.224999999999994,"2-H2"]
[null,3,11,24.574999999999999,24,0.91800000000000004,80.001999999999995,87.146000000000001,104.82,102.389,4.6118399999999999,96.224999999999994,"2-H3"]
[null,4,0.5,41.518999999999998,42.850999999999999,0.91166999999999998,79.998999999999995,87.751000000000005,105.547,96.891999999999996,5.2263000000000002,null,"7-H1"]
[null,4,1.5,36.603000000000002,37.563000000000002,0.92523999999999995,79.998999999999995,86.463999999999999,103.999,97.444000000000003,5.16425,null,"7-H2"]
[null,4,2,35.049999999999997,35.884999999999998,0.92725999999999997,79.997,86.272999999999996,103.77,97.673000000000002,5.1340000000000003,null,"13-H1"]
[null,4,3,32.781999999999996,33.392000000000003,0.93140000000000001,79.998000000000005,85.89,103.309,98.173000000000002,5.0728999999999997,null,"7-H3"]
[null,4,4,31.09,31.492999999999999,0.93125000000000002,80.001000000000005,85.906999999999996,103.33,98.718999999999994,5.012886,null,"13-H2"]
[null,4,5,29.689,29.901,0.93103000000000002,79.995999999999995,85.923000000000002,103.349,99.293000000000006,4.9537000000000004,null,"8-H1"]
[null,4,6,28.556999999999999,27.59,0.92969999999999997,79.998000000000005,86.046999999999997,103.499,99.744,4.8948499999999999,96.222999999999999,"1-H1"]
[null,4,7,27.58,27.5,0.92800000000000005,79.998000000000005,86.203000000000003,103.68600000000001,100.28,4.8371000000000004,96.222999999999999,"1-H2"]
[null,4,8,26.626999999999999,26.41,0.92610000000000003,80.004000000000005,86.388999999999996,103.91,100.81,4.78,96.23,"1-H3"]
[null,4,9,25.887,25.555,0.92390000000000005,79.998999999999995,86.585999999999999,104.14700000000001,101.3,4.7243000000000004,96.224000000000004,"2-H1"]
[null,4,10,25.033999999999999,24.513999999999999,0.92149999999999999,79.998000000000005,86.811000000000007,104.417,102.12,4.6686500000000004,96.222999999999999,"2-H2"]
[null,4,11,24.4,23.84,0.91905000000000003,80.001999999999995,87.048000000000002,104.703,102.34699999999999,4.6139599999999996,96.227000000000004,"2-H3"]
[null,5,0.5,37.503,38.715000000000003,0.92403999999999997,79.998999999999995,86.575000000000003,104.134,96.869,5.2187000000000001,null,"4-H1"]
[null,5,1.5,34.426000000000002,35.348999999999997,0.93196999999999997,80.001000000000005,85.840999999999994,103.251,97.391000000000005,5.16,null,"4-H3"]
[null,5,2,33.311999999999998,34.118000000000002,0.93267999999999995,80,85.774000000000001,103.17,97.637,5.1307299999999998,null,"13-H3"]
[null,5,3,31.577999999999999,32.177,0.93452999999999997,79.998000000000005,85.602999999999994,102.964,98.138000000000005,5.0716000000000001,null,"5-H1"]
[null,5,4,30.231999999999999,30.638000000000002,0.93340999999999996,80,85.706999999999994,103.09,98.677000000000007,5.0127300000000004,null,"14-H1"]
[null,5,5,29.038,29.254999999999999,0.93261000000000005,80,85.78,103.178,99.257000000000005,4.9541599999999999,null,"5-H2"]
[null,5,6,25.425999999999998,25.501000000000001,0.93101999999999996,80.001000000000005,85.929000000000002,103.357,99.704999999999998,4.8960999999999997]
[null,5,7,25.425999999999998,25.364999999999998,0.92908999999999997,79.998000000000005,86.103999999999999,103.56699999999999,100.24,4.8388499999999999]
[null,5,8,25.425999999999998,25.231999999999999,0.92700000000000005,80.003,86.302999999999997,103.806,100.76900000000001,4.7820900000000002]
[null,5,9,24.207999999999998,23.905000000000001,0.92466000000000004,80.004999999999995,86.524000000000001,104.072,101.267,4.7257999999999996]
[null,5,10,25.425999999999998,24.974,0.92222000000000004,80.001999999999995,86.748999999999995,104.343,101.809,4.6707900000000002]
[null,5,11,24.207999999999998,23.664000000000001,0.91962999999999995,79.998000000000005,86.99,104.63200000000001,102.29900000000001,4.61625]

{"sheet":"Instructions","index":1,"n_rows":35,"n_cols":1,"rows_kept":35,"cut":false,"hidden":false,"merged":[]}
[]
["Filter Sizing Estimator Instructions:"]
["Enter the following parameters:"]
["Non-Linear Loads"]
["1-Total Horsepower of all similar non-linear loads"]
["2-DC buss inductance % of non-linear loads (enter: 0, 1, 2, 3, 4 or 5)"]
["3-Input AC line reactor % of non-linear loads (enter: .5, 1, 2, 3, 4, 5 or 6)"]
["(Note: If DC buss inductance is less than 2% then the AC line reactance must be at least 2%)"]
["4-Acceptable TDD (I)  %"]
["5-Acceptable power factor"]
[]
["Linear Loads"]
["1-Total horsepower of all similar linear motor loads"]
["2-Power factor of linear motor loads"]
["3-Total kW of all resistive loads (power factor = 1.0)"]
[]
["To Calculate Results"]
["Left mouse button click on “Return Values from Table” button"]
["Left mouse button click on “Calculate Filter Size” button"]
[]
["Results"]
["The program will display four sets of electrical system parameters based on different levels of correction"]
["System W/O Filter"]
["Displays estimates of the electrical system parameter without any correction"]
["System with Acceptable TDD"]
["Displays estimates of the electrical system parameters with the entered acceptable TDD (I) value"]
["System with 0% TDD"]
["Displays estimates of the electrical system parameters if 0% TDD (I) is achieved"]
["System with 0% TDD and Acceptable Power Factor"]
["Displays estimates of the electrical system parameters with 0% TDD and the entered acceptable Power Factor value."]
["Estimated size of filter"]
["Displays the estimated minimum size of the required HPS TruWave (Active filter)"]
["The HPS TruWave model rating should be equal to or greater than the displayed value."]
[]
["Note:  If you have any questions regarding the use, or results, of the sizing estimator please contact the factory for assistance."]